## Slide 1: Electricity Distribution Sector Cyclone Gabrielle Review
ENA Webinar
09 October 2023

## Slide 2: Agenda
In this presentation, we cover three broad themes:
  What was the impact on customers and networks?
  What went well?
  What did we learn, and how could the sector's resilience be improved?

## Slide 3: Impact (1/3)
At its peak, 240,000 customers lost supply (11% of NZ)
In relation to the distribution sector
  Out-of-zone trees falling on lines (which are trees outside of EDBs areas of control) interrupted 67,000 customers. This was the largest single cause of outage
  Storms conditions above design limits interrupted a further 63,000 customers
  Flooding was also a material factor, impacting over 62,000 customers
(Largely transmission related)

## Slide 4: Impact (2/3)
Contributing factors
  The duration of cyclonic conditions delay restoration, and the first two days were mainly “make-safe” and network switching
  There were over 2,200 outages, many with significant damage. This created a very high demand for control room resources, field resources, and materials that would have impacted restoration time
  The outage duration was the longest for customers in Hawkes Bay and the Far North

## Slide 5: Impact (3/3)
Subtransmission and critical feeders performed well…
  Showed the benefit of prior investment in network hardening and security
  Subtransmission fault rate was less than half of distribution (1.8 vs. 4.0 outages per 100km)
  Subtransmission and critical feeders were also restored quicker (i.e. they were given a higher priority and there more alternatives available)

## Slide 6: What went well
Core network security, preparedness, and industry support kept outages to a minimum and assisted in restoring supply
What went well
Core network security—Networks have inherent redundancy in critical areas (i.e. subtransmission and feeders supplying important customers) and those areas stood-up well during the event, accounting for only 4% of outages—this shows the benefit of prior investment in network hardening
Preparedness—EDBs have robust emergency management plans and management structures. These are well tested and are continuously being improved through experience. Response actions were initiated in advance, albeit that the full scale of the event was not clear.
Pan-industry support—Restoring supply into the Hawkes Bay and Tairāwhiti took innovation and coordination by Transpower, Unison, Genesis and Firstlight—minimising the outage time
Mutual aid—When the scale of the event became clear, resources were shared across the industry to affected areas—improving restoration time
Customer communication—Despite some external telecommunication challenges, customers were kept informed using a mix of media. We received good feedback

## Slide 7: Key conclusions
Reduce the height and shorten the length of the customers–off curve!
  Reduce the number of customers lost:
  Reducing risk (minimising vulnerably of the subtransmission, zone substations and core feeders)
  Reduce exposure to out-of-zone trees
  Reduce the restoration time
  Continuous improvement in resourcing sharing and access contingency
  Strengthen the fall-back
Reducing network risk and exposure to out-of-zone trees reduces the number of customers lost
Continuous improvement in resources and access reduces the length of the tail. Community hubs as the fall-back
1
2
3
1
2
3

## Slide 8: Learnings—risk reduction (1/2)
Risk reduction was generally good, but needs to evolve further…
  The identification of hazards and assets vulnerable to them is generally robust for typical hazards…
  …but work is at an earlier stage in relation to flooding, geotechnical hazards, and assessing how hazards may alter with climate change
  Current designs performed well. EDBs apply post-disaster standards to zone substation and control room design (with minor expectations for less critical assets)
  The standards in relation to flooding (for post-disaster operations) do not appear to be as clearly defined as those applying to structural performance

## Slide 9: Learnings—risk reduction (2/2)
Risk reduction
  Pre-2000 overhead lines were designed to a lower standard
  The windspeeds experienced in some locations during Cyclone Gabrielle were highly likely to have been above the design limits for pre-2000 lines
  Current rules constrain the ability of EDBs to manage trees that present a fall-risk to lines

## Slide 10: Learnings—causes
The inability to reduce some risks and not fully recognising others drove the scale of the outage
  Out-of-zone trees were the largest cause of outages and could not be mitigated prior due to the narrow focus of the current tree regs
  The flooding damage in Hawkes Bay was significant, and that vulnerability (overtopping flood banks) was not well understood nor mitigated prior. It was also a complex restoration that took time to complete
  The significant number of outages (that was difficult to anticipate and plan for with foresight) caused resource constraints impacting restoration time—mutual aid was provided but took time to arrive
  Access restrictions, to the extent they occurred, were not anticipated

## Slide 11: Learnings—resources
Resource escalation helps, but has its limits…
  Field resource escalation has its limit. In this case due to the number of companies impacted (restricting availability), roading damage (restricting access), and logistics and management limitations within affected businesses
  Control room resource constraints were experienced in the areas where damage was greatest, but due to commonality in some control systems, resources could be transferred from SI companies to NI companies. This provide some relief, but didn’t fully resolve constraints
  Controllers resource escalation also has its limit, due to the size of the resource pool and limited buddy-support in the host company

## Slide 12: Learnings—interdependencies
Interdependencies caused delays…
  The failure of the roading network was material on the East Coast, Hawkes Bay and rural areas around Auckland. Roading damage, and lack of visibility of the roading damage, impacted planning and delayed restoration efforts
  The communications failure (due to back-haul fibre damage) on the East Coast was material and prevented customers from reporting faults. This, combined with the access issues and delays in aerial surveys, impacted restoration
  Failure of public telecommunications due to short cell-tower battery backup impacted field and network communications and delayed restoration efforts

## Slide 13: Actions to drive improvements
Drivers of improvements (more details in the report)
Specific asset upgrades, incremental improvement (as assets are renewed), and alternative arrangement (e.g. micro-grids) will reduce risks—regulatory support for resilience investments (balanced against affordability) and RMA changes to reduce the consenting hurdle for route diversity is needed
Greater rights to incentivise landowners and enable EDBs to manage trees—Revision to tree regs to better control over lines corridor to improve resilience
There are hard to access areas where restoration may be delayed—community hubs will enhance support
Continuous improvement in resourcing, access, coordination, and communication will improve outcomes for customers